## Slide 1
Bab
Keselamatan dalam Penggunaan Listrik
7

## Slide 2: Outline of talk
Electrical Terminology
How does electricity work?
Electrical quantity
Working with electricity
Electrical safety devices
Reference :
Charles A. Wentz, Safety, Health and Environmental Protection, MGH, 1998.

## Slide 3: Electrical Terminology
Electricity: Negatively Charged Particles Moving Over A Conductor
Current: Movement Of Electrons Along A Conductor
V = IR , V :voltage(V), I: current (A)
R : resistance ()
R =  L/A , : resistivity (m), L: conductor length (m), A: cross-sectional area (m2)
Fluids | Electricity
Pressure | Voltage
Flow | Current
Friction | Resistance

## Slide 4
Ground Or Grounding: The Draining Or Passage Of Electricity Into The Earth
Alternating Current: Current That Alternates Direction Through A Conductor
Direct Current: Current That Flows In The Same Direction Through A Conductor
Static Electricity: Electrical Charge Resulting From Friction Between Two Objects Or From Objects Striking

## Slide 5
Shock: Condition When The Body Becomes A Part Of A Circuit
Polarity: The Flow Of Electrons In The Proper Direction (From The Source To The Device Or Negative To The Positive Through A Device

## Slide 6: HOW DOES ELECTRICITY WORK?
Like Charges Attract; Unlike Charges Repel
Electricity: Negatively Charged Particles (Electrons) Moving Over A Conductor
Conductor: A Material With A Relatively Low Resistance To The Flow Of Electrons
Insulator: Material That Has A High Resistance To The Flow Of Electrons

## Slide 7: Electrical Quantities
Volts: A Measurement Of Electrical Pressure
Watts: A Unit Of Electrical Power
Amperes: A Measurement Of The Volume Of Electrical Current
Ohms: Measure Of The Resistance To The Flow Of Electrons

## Slide 8
WORKING WITH ELECTRICITY REQUIRES GOOD SAFETY HABITS

## Slide 9: ELECTRICITY SAFETY WORK PRACTICES
Know Where The Hazards Are
Properly Maintain Equipment
No Exposed Parts Or Energized Surfaces
Use Barriers And Devices Where Appropriate
No Conductors To Walk On Or Trip On
No Jewelry, Or Other Metal Objects Around Electricity

## Slide 10: ELECTRICAL SAFETY DEVICES
Insulation
Ground Fault Circuit Interrupters (GFCIs)
Double-Insulated Devices
Grounding (Circuit And Equipment)
Guarding
Fuses And Circuit Breakers
Personal Protective Equipment

## Slide 11: Testing is required Because “Accidents are Unacceptable”
  No one should be injured because We did not follow the rules.
ELECTRICITY SAFETY
EQUIPMENT TEST

## Slide 12
There are two sets of tests:
* DC leakage: Use a multi-meter on the highest ohms range to measure the resistance between the Hot/Neutral prongs of the wall plug (shorted together and with the power switch on where one exists) to ALL exposed metal parts of the equipment including metallic trim, knobs, connector shells and shields, VHF and UHF antenna connections, etc.
This resistance must not be less than 1 M ohm.

## Slide 13
* AC leakage:
Connect a 1.5K ohm, 10 Watt resistor in parallel with a 0.15 uF, 150 V capacitor.
With your multi-meter set on ACV across this combination and the equipment powered up, touch between a known earth ground and each exposed metal part of the equipment as above.
WARNING: Take care not to touch anything until you have confirmed that the leakage is acceptable - you could have a shocking experience!
The potential measured for any exposed metal surface must not exceed 0.75 V.

## Slide 14: Values Exceeded
If the equipment fails either of these tests,
The fault MUST be found and corrected before putting it back in service
(Even if you are doing this for your in-laws!).

## Slide 15: WORKING SAFELY WITH CORDS
Inspect Cords Before Each Use
Be Sure Plug And Receptacle Have Proper Mating Configuration
To Unplug, Never Pull On The Cord, Pull On The Plug
Don’t Use Nails, Staples, Screws, Etc, To Attach Or Fasten A Cord Or Plug

## Slide 16: WORKING SAFELY WITH CORDS
Two Conductor Cords Are Illegal
Damaged Cords Should Never Be Used
Ensure Enough Slack To Prevent Strain On Plug Or Receptacle
A Plug-Receptacle Should Have At Least 8 Ounces Of Contact Tension

## Slide 17: WORKING SAFELY WITH CORDS
Cords Should Be Kept Clean And Free Of Kinks And Insulation Breaks
Cords Crossing Vehicular Or Personnel Passageways Should Be Protected, Sign Posted, And Used Temporarily Or In An Emergency
Cords Should Be Of Continuous Length And Without Splices

## Slide 18: What can be the result of unsafe electrical practices?

## Slide 19: UNSAFE ELECTRICAL PRACTICES CAN CAUSE:
SHOCK
FIBRILATION
FIRE
DEATH
INCONVIENCE

## Slide 20: ELECTRICAL CURRENT EFFECTS ON THE HUMAN BODY

## Slide 21: ELECTRICAL SHOCK EFFECTS BASED ON THE TYPE OF CURRENT

## Slide 22: WHAT CAUSES SHOCKS?
Touching Both Wires Of An Electrical Circuit
Touching One Energized Wire And A Ground Conductor
Touching The Case Of A Faulted Or “Short” Circuited Appliance Or Machine

## Slide 23: PRINCIPAL SOURCES OF ELECTRICAL SHOCK

## Slide 24: HOW IS THE SERIOUSNESS OF AN ELECTRICAL SHOCK DETERMINED?
The Voltage (Pressure) On Circuit
Skin Resistance And Internal Resistance
Amount Of Current Flowing Through The Body, A Function Of Volts And Amps
Path The Current Takes
Body’s Reaction To The Shock
Length Of Time Electricity Is Applied

## Slide 25: ELECTRICAL RESISTANCE OF THE BODY

## Slide 26: EFFECTS OF ELECTRICAL SHOCK
Volts Divided By Resistance in Ohms = Current In Amps
120 Volts Divided By 100,000 Ohms = 0.0012 Amps Or 1.2 Milliamps
1.2 Milliamps Is Perception Threshold
10-20 Milliamps Is Painful; Let-Go Threshold; Can Kill In Time
100 Milliamps Can Kill In A Second; Can’t Let Go
200 Milliamps Kills; Causes Heart Fibrillation; Burns Human Flesh

## Slide 27: IF ELECTROCUTION OCCURS
DO NOT Touch The Victim Or The Conductor
Shut Off The Current At The Control Box
If Shutoff Not Immediately Available, Use Non-Conducting Material To Free Victim
Call For Help
If Necessary And You Know How, Begin CPR
In Dealing With Electricity, Never Exceed Your Expertise

## Slide 28: Fibrillation and resuscitation Fibrillation is the fine, rapid, erratic, movements that replace the normal contraction, as seen at left, of the vetricular muscle of the heart Fibrillation can be stopped by application of another controlled electrical shock, known as defibrillation, often seen in movies and on TV... A stopped heart can often be resuscitated with CPR techniques (cardiopulmonary resuscitation), but seldom a fibrillating heart.

## Slide 29
Electrical shorts can cause Fires

## Slide 30: Letter-shaped symbol markings are also used to indicate extinguisher suitability according to class of fire. Extinguishers suitable for Class A fires should be identified by a triangle containing the letter "A." If colored, the triangle should be green.

## Slide 31
CURRENT KILLS
(not voltage)
Current effects on human body, current through chest
(A, amps)
<0.01
tingling or imperceptible
0.02
painful, cannot let go
0.03
breathing disturbed
0.07
breathing very difficult
0.10
death due to fibrillation
>0.20
no fibrillation, but severe burning, no breathing

## Slide 32
Effects of different current levels through human body
  Current passing through victim is determined by resistance.
  Dry skin resistance is typically ~500,000 ohms.
  Wet skin resistance falls to ~1000 ohms.
  Internal resistance of body is only 100 to 500 ohms.
  Most household electrical injuries occur in the bathroom as a consequence.
  Our skin, when dry, normally protects us from electrocution if we make inadvertent contact with 115V household voltages. Not so when wet...

## Slide 33
Anything That has Energy (Electrical or Kinetic) has the Potential To be a safety hazard.
REMINDER!

## Slide 34: BEST ADVICE
Treat Electricity With
The Respect It Demands,
And It Will Serve You
Efficiently And Effectively